## Sheet1
Type | Parameter | Units | Model | Reality | % difference
Inputs | Live steam T | Cdeg | 535 | 535 | -
| Live steam P | bar | 125 | 125 | -
| Live steam m | kg/s | 38.88 | 34 | 12.5514 | Boiler flow | In the design the convergence is on the DH outlet T which is exactly 75 Cdeg
| Live steam h | kJ/kg/K | 3437 | 3437 | - | Boiler outlet h | The reason for having the design is that TRNSYS requires the calculation of heat transfers properties of the bottom cycle
| Exhaust steam p | bar | 0.259 | 0.21 | 18.9189
Outputs | Exhaust steam T | Cdeg | 65.78 | 60.9 | 7.4187
| Exhaust steam M | kg/s | 14.8 | 9.6 | 35.1351
| Exhaust steam h | kJ/kg/K | 2515 | 2361.4 | 6.1074
| Turbine power (gross) | MW | 26.53 | 29.57 | 11.4587 |  |  | Units | Model | Reference | Proportion
| Steam heat power | MW | 85 | 85 | - |  | Heated area | m2 | 48 | 4889 | 101.8542
| ECO inlet T | Cdeg | 282.6 | 224.3 | 20.6299 |  | Heating apt | kWh | 678 | - | -
| ECO inlet P | bar | 138 | 141 | 2.1739 |  | Heating building | kWh | 69057.125 | 86281 | -
| COND_DH low T | Cdeg | 70.45 | - | - |  | Difference | % | 19.9625
| COND_DH high T | Cdeg | 78.5 | 75 | 4.4586
| COND_DH Water | kg/s | 507 | 506.872 | 0.025247 | Boiler inlet h